## Summary
Project Summary ¦ EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - run
PROJECT INFORMATION
Project Name | MF8_IndSupply_IndExhaust_SZHP_HRV
Run Description | MF8 Individual Supply + Individual Exhaust (SZHP-HRV)
City / Climate Zone | Los Angeles — CZ 9
Conditioned Area | 7320 sf (residential) / 7320 sf (total)
Dwelling Units | 8
Stories | 2
Weather File | CA_Title24_2025_LOS-ANGELES-USC.epw
Software | CBECC 2025.2.0.1 (1395)
Fuel Type | NaturalGas
Model Type | MF08-VRF
SYSTEM OVERVIEW
Residential System | VRF — DuctlessVRFHeatPump - Ductless variable refrigerant flow (VRF) heat pump
Central Vent System | —
HX Type | —
Compliance Report | LMCCPRF.xml
VRF PERFORMANCE SNAPSHOT (AP vs AB)
Parameter | Proposed (AP) | Standard (AB) | AP Source | AB Source
System Type | DuctlessVRFHeatPump - Ductless variable refrigerant flow (VRF) heat pump | ASHPPM | cibd25x: ResHtPumpSys.Type | ab-cse.cse: RSYS.rsType
VRF Type | Type 2 — Ductless (per-unit) | Standard Design | cibd25x: ResHtPumpSys.Type = DuctlessVRFHeatPump | Standard design
Speed | Variable | Single Speed | cibd25x: ResHtPumpSys.Speeds | Standard design
Efficiency Metric | HSPF2/SEER2/EER2 | — | cibd25x: ResHtPumpSys.EffMetric | —
Cooling EER2 | 10.8 | 10.8 | cibd25x: ResHtPumpSys.EER2 / ap-cse perfmap | ab-cse.cse: PERFORMANCEMAP comment (EER2)
Cooling SEER2 | 14 | 14.3 | cibd25x: ResHtPumpSys.SEER2 | ab-cse.cse: PERFORMANCEMAP comment (SEER2)
Heating HSPF2 | 7 | 7.5 | cibd25x: ResHtPumpSys.HSPF2 | ab-cse.cse: PERFORMANCEMAP comment (HSPF2)
Input Rated Cooling Capacity (CIBD) (Btu/h) | Autosized (cibd25x: AutoSize=1) | Autosized (Standard Design) | cibd25x: ResHtPumpSys.AutoSize | Standard design
Input Rated Heating Capacity (CIBD) (Btu/h) | Autosized (cibd25x: AutoSize=1) | Autosized (Standard Design) | cibd25x: ResHtPumpSys.AutoSize | Standard design
Run Rated Cooling Capacity (CSE) (Btu/h) | — | Autosized | ap-cse.cse: first RSYS.rsCapC | ab-cse.cse: AUTOSIZE
Run Rated Heating Capacity (CSE) (Btu/h) | — | Autosized | ap-cse.cse: first RSYS.rsCap47 | ab-cse.cse: AUTOSIZE
Sized Cooling Capacity Range (Btu/h) | — | — | — | —
Sized Heating Capacity Range (Btu/h) | — | — | — | —
COMPLIANCE RESULT
Overall Result | PerfFails
Efficiency Margin | -0.06 kBtu/sf·yr TDV [Fail]
Total Margin | -0.02 kBtu/sf·yr TDV [Fail]
Source Margin | 7.03 kBtu/sf·yr [Pass]
% Improvement | 0%
INPUT FILES
AP HVACSecondary CSV | EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - ap - HVACSecondary.csv
AB HVACSecondary CSV | EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - ab - HVACSecondary.csv
AP HVACCAPS CSV | EX02_MF08_RES_VRF_TYPE 2_HP_CZ09 - AP-HVACCAPS.CSV
AB HVACCAPS CSV | EX02_MF08_RES_VRF_TYPE 2_HP_CZ09 - AB-HVACCAPS.CSV
AP CSE file | EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - ap-cse.cse
AB CSE file | EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - ab-cse.cse
LMCCPRF.xml | EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - LMCCPRF.xml
Model .cibd25x | EX02_MF08_Res_VRF_TYPE 2_HP_CZ09.cibd25x
AP HVACPrimary CSV | EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - ap - HVACPrimary.csv
AP XML file | EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - ap.xml
AB XML file | EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - ab.xml

## Building Systems
Building Systems ¦ EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - run
ENVELOPE
Parameter | Proposed (AP) | Standard (AB) |  | Notes
Building Wall Area (sf) [existing] | 5168 | —
New Window Area (sf) | 0 | —
Building Window Area (sf) | 821 | —
New Window-to-Wall Ratio | 0.000 | —
Building WWR | 0.159 | —
PV / BATTERY
Parameter | Prescribed | User-Specified (AP) | Standard (AB) |  | Source
PV System Size (kWdc) | — | 15.4 | 15.4 | PVBattery.csv
Battery Capacity (kWh) | — | — | — | PVBattery.csv
PV Array Type | — | — | — | pvb-cse.cse
Battery Chg/Disch kW | — | — | — | pvb-cse.cse
Battery TOU Window | — | — | — | pvb-cse.cse
PV Inverter Efficiency | — | — | — | pvb-cse.cse
PRIMARY HVAC EQUIPMENT (AP)
Equipment | Type / Fuel | Capacity | Efficiency

## Compliance Results
Compliance Results ¦ EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - run
C22 RESULT 1 — Overall Compliance (TDV kBtu/sf·yr)
End Use | Standard | Proposed | Margin (+saves) | Pass / Fail
Efficiency Compliance | 8.85 | 8.91 | -0.06 | Fail
Total Compliance | -9.4 | -9.38 | -0.02 | Fail
Source Energy | 7.22 | 0.19 | 7.03 | Pass
OVERALL RESULT: PerfFails |  |  |  | PerfFails
C22 RESULT 2 — TDV End-Use Breakdown (kBtu/sf·yr TDV)
End Use | Standard | Proposed | Margin (+saves) | Note
Heating | 0.11 | 0 | 0.11
Cooling | 1.64 | 2.24 | -0.6
Fan | 1.59 | 1.22 | 0.37
Heat Rejection | 0 | 0 | 0
Pump | 0.03 | 0.03 | 0
DHW | 5.48 | 5.42 | 0.06
Lighting | 0 | 0 | 0
EFFICIENCY SUBTOTAL | 8.85 | 8.91 | -0.06 | -0.7 % improvement
Photovoltaic (PV) | -18.25 | -18.29 | 0.04
TOTAL (incl. PV) | -9.4 | -9.38 | -0.02 | 0 % improvement
C22 RESULT 4 — Source Energy (kBtu/sf·yr source)
End Use | Standard Source | Proposed Source | Margin (+saves) | Note
Heating | 0.05 | 0 | 0.05
Cooling | 0.22 | 0.34 | -0.12
Fan | 0.37 | 0.31 | 0.06
Heat Rejection | 0 | 0 | 0
Pump | 0.02 | 0.01 | 0.01
DHW | 8.37 | 1.34 | 7.03
EFFICIENCY SUBTOTAL (Source) | 9.03 | 2 | 7.03 | 77.9 % improvement
Photovoltaic (PV) | -1.81 | -1.81 | —
TOTAL SOURCE (incl. PV) | 7.22 | 0.19 | 7.03 | 97.4 % improvement

## Res HVAC — Unit Types
Res HVAC — Unit Types ¦ EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - run
PROPOSED DESIGN (AP) — 4 unit types
Unit Type | Beds | Area (sf) | HP Config | HSPF2 | SEER2 | EER2 | Fan W/cfm | Duct Location | Sup Leak (%) | Ret Leak (%) | Duct Insul R | Distribution Config | IAQ Strategy | IAQ CFM | IAQ W/cfm | ERV Sens % | ERV Adj % | Aux Heat Type | HP Lockout (°F) | DHW System | Cook Fuel | Htg Cap Range (kBtu) | Clg Cap Range (kBtu)
1-Bedroom | 1 | 750 | DuctlessVRFHeatPump - Ductless variable refrigerant flow (VRF) heat pump | 7 | 14 | — | 0.171 | Ducts in conditioned space | 4.09 | 2.9 | 4.2 | not compact | Individual IAQ Fans | 37.5 | 0.4 | 70 | 70 | Resistance | -30 | — | Electricity | — | —
1-Bedroom | 1 | 750 | DuctlessVRFHeatPump - Ductless variable refrigerant flow (VRF) heat pump | 7 | 14 | — | 0.171 | Ducts in conditioned space | 4.09 | 2.9 | 4.2 | not compact | Individual IAQ Fans | 37.5 | 0.4 | 70 | 70 | Resistance | -30 | — | Electricity | — | —
2-Bedroom | 2 | 1080 | DuctlessVRFHeatPump - Ductless variable refrigerant flow (VRF) heat pump | 7 | 14 | — | 0.171 | Ducts in conditioned space | 4.09 | 2.9 | 4.2 | not compact | Individual IAQ Fans | 54.9 | 0.4 | 70 | 70 | Resistance | -30 | — | Electricity | — | —
2-Bedroom | 2 | 1080 | DuctlessVRFHeatPump - Ductless variable refrigerant flow (VRF) heat pump | 7 | 14 | — | 0.171 | Ducts in conditioned space | 4.09 | 2.9 | 4.2 | not compact | Individual IAQ Fans | 54.9 | 0.4 | 70 | 70 | Resistance | -30 | — | Electricity | — | —
ℹ Residential AP and AB systems use identical efficiency and duct parameters — HP ratings, fan W/cfm, and duct leakage are the same in both designs.
STANDARD DESIGN (AB) — 4 unit types (same params as AP)
Unit Type | Beds | Area (sf) | HP Config | HSPF2 | SEER2 | EER2 | Fan W/cfm | Duct Location | Sup Leak (%) | Ret Leak (%) | Duct Insul R | Distribution Config | IAQ Strategy | IAQ CFM | IAQ W/cfm | ERV Sens % | ERV Adj % | Aux Heat Type | HP Lockout (°F) | DHW System | Cook Fuel | Htg Cap Range (kBtu) | Clg Cap Range (kBtu)
1-Bedroom | 1 | 750 | DuctlessVRFHeatPump - Ductless variable refrigerant flow (VRF) heat pump | 7 | 14 | — | 0.171 | Ducts in conditioned space | 4.09 | 2.9 | 4.2 | not compact | Individual IAQ Fans | 37.5 | 0.4 | 70 | 70 | Resistance | -30 | — | Electricity | — | —
1-Bedroom | 1 | 750 | DuctlessVRFHeatPump - Ductless variable refrigerant flow (VRF) heat pump | 7 | 14 | — | 0.171 | Ducts in conditioned space | 4.09 | 2.9 | 4.2 | not compact | Individual IAQ Fans | 37.5 | 0.4 | 70 | 70 | Resistance | -30 | — | Electricity | — | —
2-Bedroom | 2 | 1080 | DuctlessVRFHeatPump - Ductless variable refrigerant flow (VRF) heat pump | 7 | 14 | — | 0.171 | Ducts in conditioned space | 4.09 | 2.9 | 4.2 | not compact | Individual IAQ Fans | 54.9 | 0.4 | 70 | 70 | Resistance | -30 | — | Electricity | — | —
2-Bedroom | 2 | 1080 | DuctlessVRFHeatPump - Ductless variable refrigerant flow (VRF) heat pump | 7 | 14 | — | 0.171 | Ducts in conditioned space | 4.09 | 2.9 | 4.2 | not compact | Individual IAQ Fans | 54.9 | 0.4 | 70 | 70 | Resistance | -30 | — | Electricity | — | —

## Res HVAC — Zones
Res HVAC — Zone Capacities (Auto-Sized) ¦ EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - run
ℹ Capacities auto-sized by CSE — vary by floor and orientation. Per-unit capacity = zone capacity ÷ units per zone.
PROPOSED DESIGN (AP) — 0 zones
# | Floor | Zone Name | Unit Type | Units/ Zone | Zone Area (sf) | Unit Area (sf) | Htg Cap — Zone (kBtu/hr) | Htg Cap — Unit (kBtu/hr) | Clg Cap — Zone (kBtu/hr) | Clg Cap — Unit (kBtu/hr)
STANDARD DESIGN (AB) — 0 zones
# | Floor | Zone Name | Unit Type | Units/ Zone | Zone Area (sf) | Unit Area (sf) | Htg Cap — Zone (kBtu/hr) | Htg Cap — Unit (kBtu/hr) | Clg Cap — Zone (kBtu/hr) | Clg Cap — Unit (kBtu/hr)

## DHW & IAQ Ventilation
DHW & IAQ Ventilation ¦ EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - run
CENTRAL DHW SYSTEM
Parameter | Value
Central DHW Type | —
System Description | Single Pass Primary
HPWH Compressor Type | Sanden GS3-45HPA-US (4kW cap @ 40F)
Number of Compressors | 2
Total Tank Volume (gal) | 160
Tank Count | 1
Tank Location | Outside
Source Air Location | Outside
Loop Tank Type | Electric Resistance
Loop Tank Volume (gal) | 80
Demand Response | Basic
CENTRAL VENTILATION SYSTEM (DOAS / HRV)
Parameter | Value (cibd25x) | Value (CSE)
System Name | — | —
Type | — | —
Supply Fan W/cfm | — | —
Exhaust Fan W/cfm | — | —
HX Type | — | —
HX Bypass | — | —
Temp Control | — | —
Htg Coil Type | — | —
Clg Coil Type | — | —
IAQ EXHAUST FANS — 2 fans defined
Fan Name | Type | CFM | W/cfm | ERV? | Sensible Recov Eff (%)
IAQ Bal Fan HRV - 1BR | Balanced | 37.5 | 0.4 | Yes | 70
IAQ Bal Fan HRV - 2BR | Balanced | 54.9 | 0.4 | Yes | 70

## Dwelling Units
Dwelling Units ¦ EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - run
DWELLING UNIT TYPES — 4 types defined
Unit Type Name | Beds | Area (sf) | Cook Fuel | Dryer Fuel | IAQ Option | Distribution Config | IAQ Fan Ref | DHW System Ref | Notes
1-Bed Type Z1 | 1 | 750 | Electricity | Electricity | Individual IAQ Fans | not compact | IAQ Bal Fan HRV - 1BR | DHWHeatpump
2-Bed Type Z1 | 2 | 1080 | Electricity | Electricity | Individual IAQ Fans | not compact | IAQ Bal Fan HRV - 2BR | DHWHeatpump
1-Bed Type Z2 | 1 | 750 | Electricity | Electricity | Individual IAQ Fans | not compact | IAQ Bal Fan HRV - 1BR | DHWHeatpump
2-Bed Type Z2 | 2 | 1080 | Electricity | Electricity | Individual IAQ Fans | not compact | IAQ Bal Fan HRV - 2BR | DHWHeatpump

## Data Sources
Data Sources & Input Files ¦ EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - run
DETECTED MODE: MF08-SZHP
Category | File Key | Full Path | Found? | Note
NR HVAC CSVs | ap_secondary | c:\github\P-SCE-Complex_HVAC\Final Data Set\EX02_MF_Central-VRF-HP\EX02_MF08_Central_VRF_HP_CZ09\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - run\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - ap - HVACSecondary.csv | Yes | AP HVACSecondary.csv
NR HVAC CSVs | ab_secondary | c:\github\P-SCE-Complex_HVAC\Final Data Set\EX02_MF_Central-VRF-HP\EX02_MF08_Central_VRF_HP_CZ09\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - run\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - ab - HVACSecondary.csv | Yes | AB HVACSecondary.csv
NR HVAC CSVs | ap_ventilation | c:\github\P-SCE-Complex_HVAC\Final Data Set\EX02_MF_Central-VRF-HP\EX02_MF08_Central_VRF_HP_CZ09\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - run\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - ap - VentilationExhaust.csv | Yes | AP VentilationExhaust.csv
NR HVAC CSVs | ab_ventilation | c:\github\P-SCE-Complex_HVAC\Final Data Set\EX02_MF_Central-VRF-HP\EX02_MF08_Central_VRF_HP_CZ09\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - run\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - ab - VentilationExhaust.csv | Yes | AB VentilationExhaust.csv
Res HVAC CSVs | ap_hvaccaps | c:\github\P-SCE-Complex_HVAC\Final Data Set\EX02_MF_Central-VRF-HP\EX02_MF08_Central_VRF_HP_CZ09\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - run\EX02_MF08_RES_VRF_TYPE 2_HP_CZ09 - AP-HVACCAPS.CSV | Yes | AP-HVACCAPS.CSV
Res HVAC CSVs | ab_hvaccaps | c:\github\P-SCE-Complex_HVAC\Final Data Set\EX02_MF_Central-VRF-HP\EX02_MF08_Central_VRF_HP_CZ09\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - run\EX02_MF08_RES_VRF_TYPE 2_HP_CZ09 - AB-HVACCAPS.CSV | Yes | AB-HVACCAPS.CSV
Res HVAC CSVs | ap_zone_areas | c:\github\P-SCE-Complex_HVAC\Final Data Set\EX02_MF_Central-VRF-HP\EX02_MF08_Central_VRF_HP_CZ09\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - run\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - ap - CSE Zone Areas.csv | Yes | AP CSE Zone Areas.csv
Envelope | ap_envelope | c:\github\P-SCE-Complex_HVAC\Final Data Set\EX02_MF_Central-VRF-HP\EX02_MF08_Central_VRF_HP_CZ09\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - run\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - ap - Envelope.csv | Yes | AP Envelope.csv
Envelope | ab_envelope | c:\github\P-SCE-Complex_HVAC\Final Data Set\EX02_MF_Central-VRF-HP\EX02_MF08_Central_VRF_HP_CZ09\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - run\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - ab - Envelope.csv | Yes | AB Envelope.csv
Primary HVAC | ap_hvacprimary | c:\github\P-SCE-Complex_HVAC\Final Data Set\EX02_MF_Central-VRF-HP\EX02_MF08_Central_VRF_HP_CZ09\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - run\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - ap - HVACPrimary.csv | Yes | AP HVACPrimary.csv
PV/Battery | ap_pvbattery | c:\github\P-SCE-Complex_HVAC\Final Data Set\EX02_MF_Central-VRF-HP\EX02_MF08_Central_VRF_HP_CZ09\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - run\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - ap - PVBattery.csv | Yes | AP PVBattery.csv
PV/Battery | ab_pvbattery | c:\github\P-SCE-Complex_HVAC\Final Data Set\EX02_MF_Central-VRF-HP\EX02_MF08_Central_VRF_HP_CZ09\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - run\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - ab - PVBattery.csv | Yes | AB PVBattery.csv
WSHP Plant | ap_plantlds | — | No | AP-CSE-PLANTLDS.CSV
CSE Files | ap_cse | c:\github\P-SCE-Complex_HVAC\Final Data Set\EX02_MF_Central-VRF-HP\EX02_MF08_Central_VRF_HP_CZ09\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - run\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - ap-cse.cse | Yes | ap-cse.cse
CSE Files | ab_cse | c:\github\P-SCE-Complex_HVAC\Final Data Set\EX02_MF_Central-VRF-HP\EX02_MF08_Central_VRF_HP_CZ09\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - run\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - ab-cse.cse | Yes | ab-cse.cse
CSE Files | ap_pvb_cse | — | No | ap-pvb-cse.cse
CSE Files | ab_pvb_cse | — | No | ab-pvb-cse.cse
Compliance XML | nrccprf | — | No | NRCCPRF.xml
Compliance XML | lmccprf | c:\github\P-SCE-Complex_HVAC\Final Data Set\EX02_MF_Central-VRF-HP\EX02_MF08_Central_VRF_HP_CZ09\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09 - LMCCPRF.xml | Yes | LMCCPRF.xml
Model Input | cibd25x | c:\github\P-SCE-Complex_HVAC\Final Data Set\EX02_MF_Central-VRF-HP\EX02_MF08_Central_VRF_HP_CZ09\EX02_MF08_Res_VRF_TYPE 2_HP_CZ09.cibd25x | Yes | *.cibd25x
COMPLIANCE REPORT KEY VALUES
project_name | MF8_IndSupply_IndExhaust_SZHP_HRV
run_desc | MF8 Individual Supply + Individual Exhaust (SZHP-HRV)
city | Los Angeles
climate_zone | 9
software | CBECC 2025.2.0.1 (1395)
units | 8
cond_area | 7320
stories | 2
fuel_type | NaturalGas
weather_file | CA_Title24_2025_LOS-ANGELES-USC.epw
nrcond_area | 7320
result_overall | PerfFails
std_eff | 8.85
prop_eff | 8.91
margin_eff | -0.06
pass_eff | Fail
std_total | -9.4
prop_total | -9.38
margin_total | -0.02
pass_total | Fail
std_source | 7.22
prop_source | 0.19
margin_source | 7.03
pass_source | Pass
eu_htg_std | 0.11
eu_htg_prop | 0
eu_htg_margin | 0.11
eu_clg_std | 1.64
eu_clg_prop | 2.24
eu_clg_margin | -0.6
eu_fan_std | 1.59
eu_fan_prop | 1.22
eu_fan_margin | 0.37
eu_hr_std | 0
eu_hr_prop | 0
eu_hr_margin | 0
eu_pump_std | 0.03
eu_pump_prop | 0.03
eu_pump_margin | 0
eu_dhw_std | 5.48